# TEESTA ELECTRO WORKS LTD.

Plot 8, Tejgaon Industrial Area, Dhaka 1208 · Dummy vendor created for the IUT alumni AI Session

Offer No: TEW/OF/2026/311
Date: 17 September 2026
Attention: Procurement Department, Meghna Knit Composite Ltd., Gazipur
Subject: Techno-commercial offer against RFQ/ENG/2026/118

## 1. Price schedule

| Sl | Item | Qty | Price (BDT) |
| --- | --- | --- | --- |
| 1 | Transformer 500 kVA, 11/0.415 kV, Dyn11, ONAN, Cu winding, OCTC ±2×2.5% (IEC 60076) | 1 | 52,40,000 |
| 2 | HT switchgear: VCB 630 A, 20 kA 3 s, numerical protection relay | 1 | 22,60,000 |
| 3 | LT distribution panel, 1000 A ACB + 2×400 A + 4×250 A MCCB, MFM | 1 | 18,90,000 |
| 4 | Automatic PFI 300 kVAR, 6 steps, 7% detuned reactors, target PF 0.97 | 1 | 13,10,000 |
| 5 | IP54 outdoor enclosure, erection, earthing (≤ 1 Ω with test report), testing, commissioning | 1 | 17,00,000 |
|  | Total (VAT and AIT extra) |  | 1,24,00,000 |

## 2. Technical particulars

- Guaranteed no-load loss: 780 W. Guaranteed load loss at 75 °C: 5,300 W.

- Enclosure suitable for 45 °C ambient and 95% RH.

- Installation per BNBC 2020 Part 8 and Bangladesh Electricity Rules.

- Type test reports: KEMA, 2023 (transformer) and 2024 (VCB), enclosed.

- Manufacturer’s authorisation letters enclosed.

## 3. Commercial terms

- Delivery: 12 weeks from work order, including commissioning.

- Warranty: 24 months from commissioning.

- Service: Tejgaon service centre (approx. 35 km from Konabari), 24-hour fault response.

- Validity: 90 days.

- Payment: 50% advance against bank guarantee, 40% on delivery, 10% after commissioning.

- Liquidated damages: accepted as per RFQ.

For Teesta Electro Works Ltd.
Engr. Sadia Rahman, Head of Projects